## Slide 1
01 / MAINS SUPPLY & DISTRIBUTION
Two independent Omron channels • Shared 24 V supply • Editable schematic
AC INPUT
DISTRIBUTION / X1
POWER SUPPLY & TWO CONTROLLER BRANCHES
L
N
PE
J1 SCHURTER
DD11.0111.1110
C14 inlet · switch · fuse
Manufacturer datasheet ↗
PE CHASSIS
Enclosure / door / DIN rail
X1 AC DISTRIBUTION
L / N / PE
Logical bus · terminals TBD
BRANCH / CH 1
BRANCH / CH 2
X1 jumpers: TBD
PS1 MEAN WELL
XDR-120E-24 · 24 V / 5 A
Shared 24 V DC supply
Manufacturer datasheet ↗
S1-A SELECTOR
DATA ↗
Schneider XB5AD23
E1 OMRON
DATA ↗
E5CC-TQX3A5M-000
A · NO 13–14
230 V AC input
S2-A SELECTOR
DATA ↗
Schneider XB5AD23
E2 OMRON
DATA ↗
E5CC-TQX3A5M-003
A · NO 13–14
230 V AC input
L
N
PE
L IN
N IN
PE IN
PE
PE
L
N
PE
C1
C2
C3
A1 +Vo
A2 −Vo
A3 −Vo
L1
N1
13
14
11
12
L2
N2
13
14
11
12
TO SHARED PSU
CH 1 CONTROLLER
CH 2 CONTROLLER
24 V OUTPUT → SHEET 02
DESIGN REVIEW ONLY — Not approved for wiring / energising
Confirm X1 terminal blocks and jumpers, DD11 output tabs / fuse, PE bonds, and 24 V interlock design.
HEATING RATE CONTROLLER / D12 SOCKET + ACTIVITY LED / EDITABLE POWERPOINT
SHEET 01 / 01

## Slide 2
02 / SHARED 24 V DISTRIBUTION & CHANNEL INTERLOCKS
One shared Mean Well supply; S1-B and S2-B independently enable their respective 24 V branches.
24 V DC DISTRIBUTION / CHANNEL 1 + CHANNEL 2
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 02
Selector terminal references: A = 13–14 (AC) | B = 23–24* (gated +24 V).
* IEC design labels only. Confirm stamps on the actual XB5AD23 contact-block assembly before wiring; X2–X4 distribution hardware remains TBD.
PS1 MEAN WELL
XDR-120E-24
24 V DC / 5 A shared supply
Manufacturer datasheet ↗
X2 DC DISTR.
+24 V / 0 V
Physical terminals and jumpers TBD
S1-B SELECTOR
XB5AD23
Manufacturer datasheet ↗
X3 CH1 CONTROL
Gated +24 V / 0 V
S2-B SELECTOR
XB5AD23
Manufacturer datasheet ↗
X4 CH2 CONTROL
Gated +24 V / 0 V
+Vo
24+
-Vo
0 V
24+
23
23
24
24
+24
0 V
0 V
24+
23
23
24
24
+24
0 V
0 V
CH1: 24 V gated by S1-B | shared 0 V below selector
CH2: 24 V gated by S2-B | shared 0 V below selector
+24 V / gated
0 V return
B · NO 23–24*
B · NO 23–24*

## Slide 3
03 / CHANNEL 1 / MOMENTARY ENABLE & FINDER CONTROL
EAO button pulses the Finder 13.61; its output enables the existing Finder 62.31 heater relay (CH1).
HEATER ENABLE CIRCUIT / 24 V DC
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 03
OFF-on-power-restoration and exact Finder supply/trigger/socket terminal markings remain to be verified.
X3 CH1 CONTROL
Gated +24 V / 0 V
SB1 EAO + LED
82-4151.1134
Manufacturer datasheet ↗
K1 FINDER 13.61
13.61.0.024.0000
Manufacturer datasheet ↗
K3 / SK3 RELAY + SOCKET
62.31.9.024.4800
92.03 socket family; actual fitted type TBD
Relay PDF ↗
Socket PDF ↗
A1/A2 are SOCKET coil labels
+24
C
0 V
LED−
NO
3
+24
L/+
11
14
A1
0 V
N/−
A2
LED+
EN1
EN1
EN1: K1:14 / K3:A1 / SB1:LED+
Matching EN reference indicates ONE electrical net (avoids a wire crossing other circuits).
X3:+24 → button C and K1 L/+,11 | Button NO → K1:3 | EN1 → relay coil A1 and LED+ | 0V → K1:N/−, K3:A2, LED−
Gated +24 V
0 V return
Momentary input

## Slide 4
04 / CHANNEL 2 / MOMENTARY ENABLE & FINDER CONTROL
EAO button pulses the Finder 13.61; its output enables the existing Finder 62.31 heater relay (CH2).
HEATER ENABLE CIRCUIT / 24 V DC
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 04
OFF-on-power-restoration and exact Finder supply/trigger/socket terminal markings remain to be verified.
X4 CH2 CONTROL
Gated +24 V / 0 V
SB2 EAO + LED
82-4151.1134
Manufacturer datasheet ↗
K2 FINDER 13.61
13.61.0.024.0000
Manufacturer datasheet ↗
K4 / SK4 RELAY + SOCKET
62.31.9.024.4800
92.03 socket family; actual fitted type TBD
Relay PDF ↗
Socket PDF ↗
A1/A2 are SOCKET coil labels
+24
C
0 V
LED−
NO
3
+24
L/+
11
14
A1
0 V
N/−
A2
LED+
EN2
EN2
EN2: K2:14 / K4:A1 / SB2:LED+
Matching EN reference indicates ONE electrical net (avoids a wire crossing other circuits).
X4:+24 → button C and K2 L/+,11 | Button NO → K2:3 | EN2 → relay coil A1 and LED+ | 0V → K2:N/−, K4:A2, LED−
Gated +24 V
0 V return
Momentary input

## Slide 5
05 / CHANNEL 1 / SSR DRIVE + HEATER ACTIVITY LED
Omron 12 V SSR demand controls an isolated Weidmüller interface switching both Crydom input and activity LED.
THERMOCOUPLE / PULSE INTERFACE / TWO PARALLEL 24 V LOADS
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 05
LED is on the 24 V CONTROL circuit, not the external heater: HL1/HL2 = RS 130-1086, yellow, 24 V DC, 20 mA max.
JTC1 TYPE K
External sensor
Connector model TBD
E1 OMRON
E5CC-TQX3A5M-000
12 V SSR demand output; TC input
Manufacturer datasheet ↗
W1 WEIDMÜLLER
8950770000
Transistor switch 13 (+) / 14 (−)
Manufacturer datasheet ↗
SSR1 CRYDOM
DR2220D30U
24 V control input (3+/4−)
Manufacturer datasheet ↗
HL1 ACTIVITY LED
24 V DC, integrated resistor
RS 130-1086 • 20 mA max
X3 GATED +24
From selector
X2 0 V RETURN
Shared control return
TC+
6+
TC−
5−
1+
A1
2−
A2
+24
+3
LED+
−4
LED−
13+
14−
0 V
W13: switched returns | W14: 0 V
Lamp follows heater demand; it does NOT measure actual heater current.
Datasheet budget: SSR max 15 mA + HL yellow LED max 20 mA = 35 mA per channel; W1/W2 DC1 output max 100 mA. Verify live circuit.
TC / 12 V demand
24 V to both loads
Switched return

## Slide 6
06 / CHANNEL 2 / SSR DRIVE + HEATER ACTIVITY LED
Omron 12 V SSR demand controls an isolated Weidmüller interface switching both Crydom input and activity LED.
THERMOCOUPLE / PULSE INTERFACE / TWO PARALLEL 24 V LOADS
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 06
LED is on the 24 V CONTROL circuit, not the external heater: HL1/HL2 = RS 130-1086, yellow, 24 V DC, 20 mA max.
JTC2 TYPE K
External sensor
Connector model TBD
E2 OMRON
E5CC-TQX3A5M-003
12 V SSR demand output; TC input
Manufacturer datasheet ↗
W2 WEIDMÜLLER
8950770000
Transistor switch 13 (+) / 14 (−)
Manufacturer datasheet ↗
SSR2 CRYDOM
DR2220D30U
24 V control input (3+/4−)
Manufacturer datasheet ↗
HL2 ACTIVITY LED
24 V DC, integrated resistor
RS 130-1086 • 20 mA max
X4 GATED +24
From selector
X2 0 V RETURN
Shared control return
TC+
6+
TC−
5−
1+
A1
2−
A2
+24
+3
LED+
−4
LED−
13+
14−
0 V
W13: switched returns | W14: 0 V
Lamp follows heater demand; it does NOT measure actual heater current.
Datasheet budget: SSR max 15 mA + HL yellow LED max 20 mA = 35 mA per channel; W1/W2 DC1 output max 100 mA. Verify live circuit.
TC / 12 V demand
24 V to both loads
Switched return

## Slide 7
07 / CHANNEL 1 / COMPLETE DC HEATER POWER LOOP
External 0–60 V DC supply, breaker, polarity-sensitive Finder DC relay, Crydom SSR and direct return.
INDEPENDENT HEATER SUPPLY / 15 A MAX DESIGN
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 07
Finder contact 34 (+) → 14 (−) and SSR load +1 → −2 are both in the POSITIVE current path.
JP1-IN DC SUPPLY
0–60 V / up to 15 A
Connector & cable TBD
QF1 LOVATO
P1MB1PC16
16 A / 80 V DC MCB
Manufacturer datasheet ↗
K3/SK3 62.31
62.31.9.024.4800
92.03-family socket; actual type TBD
Manufacturer datasheet ↗
SSR1 CRYDOM
DR2220D30U
Solid-state DC switch
Manufacturer datasheet ↗
JP1-OUT HEATER
External resistive load
Connector & cable TBD
DC+
1
P1-01
2
34+
P1-02
14−
+1
P1-03
−2
H+
P1-04
SSR
NO contact
Electronic switch
DC−
H−
DC NEGATIVE RETURN — SEPARATE FROM SWITCHED POSITIVE
Finder terminal 14 (−) and SSR load −2 remain in the POSITIVE conductor — neither is the supply 0 V. Breaker coordination, socket/contact derating and SSR heat dissipation require design approval.
Switched positive
Separate DC− return

## Slide 8
08 / CHANNEL 2 / COMPLETE DC HEATER POWER LOOP
External 0–60 V DC supply, breaker, polarity-sensitive Finder DC relay, Crydom SSR and direct return.
INDEPENDENT HEATER SUPPLY / 15 A MAX DESIGN
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 08
Finder contact 34 (+) → 14 (−) and SSR load +1 → −2 are both in the POSITIVE current path.
JP2-IN DC SUPPLY
0–60 V / up to 15 A
Connector & cable TBD
QF2 LOVATO
P1MB1PC16
16 A / 80 V DC MCB
Manufacturer datasheet ↗
K4/SK4 62.31
62.31.9.024.4800
92.03-family socket; actual type TBD
Manufacturer datasheet ↗
SSR2 CRYDOM
DR2220D30U
Solid-state DC switch
Manufacturer datasheet ↗
JP2-OUT HEATER
External resistive load
Connector & cable TBD
DC+
1
P2-01
2
34+
P2-02
14−
+1
P2-03
−2
H+
P2-04
SSR
NO contact
Electronic switch
DC−
H−
DC NEGATIVE RETURN — SEPARATE FROM SWITCHED POSITIVE
Finder terminal 14 (−) and SSR load −2 remain in the POSITIVE conductor — neither is the supply 0 V. Breaker coordination, socket/contact derating and SSR heat dissipation require design approval.
Switched positive
Separate DC− return

## Slide 9
09 / CONNECTION SCHEDULE / MAINS + 24 V DISTRIBUTION
Functional point-to-point net destinations for the component-port diagrams (not a physical ferrule/cable schedule).
TERMINAL-LEVEL REFERENCE / MAINS AND 24 V
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 09
Any X1–X4 numbers are logical net references until actual terminal blocks/jumpers are documented.
AC01
J1 switched fused L
→
X1:L bus
AC02
J1 switched N
→
X1:N bus
AC03
J1:PE
→
X1:PE + chassis bonds
AC04
X1:L / N / PE
→
PS1:C1 / C2 / C3
AC05
X1:L → S1-A:13/14
→
E1:11 (L)
AC06
X1:N bus
→
E1:12 (N)
AC07
X1:L → S2-A:13/14
→
E2:11 (L)
AC08
X1:N bus
→
E2:12 (N)
DC01
PS1:A1 +Vo
→
X2:+24 V shared
DC02
PS1:A2/A3 −Vo
→
X2:0 V shared
DC03
X2:+24 → S1-B:23/24*
→
X3:CH1 gated +24
DC04
X2:+24 → S2-B:23/24*
→
X4:CH2 gated +24
DC05
X2:0 V shared
→
X3 / X4 returns
Before wiring: confirm selector B contact-block stamps (*23/24 IEC proposed), J1 tabs, PE, X1–X4 blocks/jumpers and mains/24 V fuses.

## Slide 10
10 / CONNECTION SCHEDULE / CONTROLS + HEATER
Both channels follow equivalent functional nets; this summary complements the illustrated component-port sheets.
TERMINAL-LEVEL REFERENCE / CHANNELS 1 AND 2
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 10
The Finder 13.61 power-up OFF state, switch actual terminals and DC protection must still be verified.
ENABLE / EACH CH
X3/4:+24 → Finder 13.61 power & 11; button C. X2:0V → Finder supply return, SK3/4:A2 and EAO LED−.
MOMENTARY INPUT
EAO SB1/2:NO → Finder K1/2:3 impulse; EAO C uses channel-gated +24 V.
FINDER OUTPUT
K1/2:14 (NO) → Finder 62.31 SOCKET SK3/4:A1 and EAO LED+; 11 COM fed from gated +24 V.
THERMOCOUPLE
Type K sensor (+) → E1/E2:6; sensor (−) → E1/E2:5.
OMRON / WEIDMÜLLER
E1/E2 SSR pulse terminals 1 (+),2 (−) → W1/W2 A1 (+),A2 (−).
WEID / SSR DRIVE
Gated +24 → SSR+3 AND activity HL+; SSR−4 AND activity HL− → W:13; W:14 → 0V.
DC POSITIVE
Supply DC+ → Lovato 1→2 → Finder 62.31 contact 34 (+)→14 (−) → SSR +1→−2 → heater+.
DC RETURN
Heater− → matching external DC supply−; Finder 14 and SSR −2 are NOT DC−.
DC COIL
Finder 62.31 uses socket SK3/4: coil A1/A2, contact 34(+)/14(−). Actual 92.03 suffix and suppressor TBD.
These are net-level circuit proposals, NOT numbered physical wires. Final wire IDs, conductor sizes, terminations and current ratings remain to be assigned.

## Slide 11
11 / MANUFACTURER DOCUMENTS & RELEASE CHECKS
Clickable component documents are embedded inside each named component block throughout the PowerPoint.
COMPONENT REGISTER / TECHNICAL REVIEW
DESIGN REVIEW ONLY | Terminal references are proposed where physical hardware is unidentified. Not approved for wiring / energising.
HEATING RATE CONTROLLER / D12 BLOCK + PORT SCHEMATICS / EDITABLE POWERPOINT
SHEET 11
Manufacturer sources are reference points, not proof that the integrated design has passed electrical safety review.
Schurter DD11.0111.1110
Datasheet ↗
Mean Well XDR-120E-24
Datasheet ↗
Schneider XB5AD23 ×2
Datasheet ↗
Omron E5CC-TQX3A5M-000 / -003
Datasheet ↗
EAO 82-4151.1134 ×2
Datasheet ↗
Finder 13.61.0.024.0000 ×2
Datasheet ↗
Finder 62.31.9.024.4800 ×2
Datasheet ↗
Weidmüller 8950770000 ×2
Datasheet ↗
Crydom DR2220D30U ×2
Datasheet ↗
Lovato P1MB1PC16 ×2
Datasheet ↗
REMAINING DESIGN-RELEASE BLOCKERS
01
Finder 13.61 must remain OFF after loss and restoration of 24 V; prove minimum interruption and button held states.
02
Confirm X1–X4 blocks, Schneider S1/S2 B-contact terminal stamps (23/24* IEC intended), J1 tabs and Finder 62.31 sockets.
03
Verify 15 A DC continuity ratings, breaker/source fault coordination, cable size and connector ratings.
04
Validate SSR heat sink, W1/W2 100 mA output (SSR+LED 35 mA max calculated), PE and emergency disconnection.
05
Independent safety design review and pre-energisation electrical/function tests by a suitably competent person.
HL1/HL2 specified: RS PRO 130-1086 yellow LED, 24 V DC, max 20 mA, IP67; 14 mm mounting hole.
Finder 92.03-series socket datasheet (actual fitted socket still unverified) ↗