## Slide 1
01 / DISTRIBUTION REQUIREMENTS / PTFIX REFERENCE
Terminal capacity for a complete two-channel installation. Every conductor gets its own connection position.
ELEVEN SEPARATE GROUPS / 48 OCCUPIED TERMINALS / 22 SPARE POSITIONS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 01 / 14
GROUP
FUNCTION
REQUIRED CONNECTIONS
USED/PORTS
SPECIFIED DIN DISTRIBUTOR
X1-L
Mains L
1 inlet + 3 outgoing
4 / 6
6X2.5 NS35 BN · 3273010
X1-N
Mains N
1 inlet + 3 outgoing
4 / 6
6X2.5 NS35 BU · 3273002
X1-PE
Protective earth
Inlet, PSU, body, door
4 / 4
WAGO 2002-1407 (PE)
X2-24
Common +24 V
PSU + two selectors
3 / 6
6X2.5 NS35 RD · 3273004
X2-0V
Common 0 V
PSU + eight returns
9 / 12
12X2.5 NS35 GY · 3273022
X3-24G
CH1 gated +24
S1-B output + 3 loads
4 / 6
6X2.5 NS35 RD · 3273004
X3-EN1
CH1 enable +24
Finder 14 + 4 loads
5 / 6
6X2.5 NS35 OG · 3273018
X3-DRV1
CH1 drive return
Weidmüller 13 + 2 loads
3 / 6
6X2.5 NS35 VT · 3273016
X4-24G
CH2 gated +24
S2-B output + 3 loads
4 / 6
6X2.5 NS35 RD · 3273004
X4-EN2
CH2 enable +24
Finder 14 + 4 loads
5 / 6
6X2.5 NS35 OG · 3273018
X4-DRV2
CH2 drive return
Weidmüller 13 + 2 loads
3 / 6
6X2.5 NS35 VT · 3273016
SPECIFIED DISTRIBUTOR QUANTITIES
PTFIX 6-way: BN ×1; BU ×1; RD ×3; OG ×2; VT ×2. PTFIX 12-way: GY ×1. WAGO PE 4-way: ×1.
Quantities are reference-design pieces, not supplier pack sizes. Separate mains, PE and 24 V wiring.

## Slide 2
02 / TERMINAL ASSIGNMENTS / MAINS + COMMON DC
Logical identification for the specified DIN terminals. Wire labels are unique within each block.
X1 = MAINS / PE • X2 = COMMON CONTROL SUPPLY
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 02 / 14
X1-L / MAINS LIVE
6 terminals, 4 used
L.1
J1 switched/fused AC live
L.2
PS1:C1 (L)
L.3
S1-A:13, Omron E1 feed
L.4
S2-A:13, Omron E2 feed
X1-N / MAINS NEUTRAL
6 terminals, 4 used
N.1
J1 switched AC neutral
N.2
PS1:C2 (N)
N.3
Omron E1:12
N.4
Omron E2:12
X1-PE / PROTECTIVE EARTH
4 positions, 4 used
PE.1
J1 inlet PE
PE.2
PS1:C3 (PE)
PE.3
Cabinet metalwork bonding lead
PE.4
Flexible door bonding strap
X2-24 / UNSWITCHED +24 V
6 terminals, 3 used
24.1
PS1:A1 (+Vo)
24.2
S1-B:23 (CH1 selector)
24.3
S2-B:23 (CH2 selector)
X2-0V / COMMON 0 V
12 terminals, 9 used
0V.1
PS1:A2 or A3 (−Vo)
0V.2
K1:N/−
0V.3
SK3:A2 (62.31 coil)
0V.4
SB1:LED−
0V.5
W1:14(−)
0V.6
K2:N/−
0V.7
SK4:A2 (62.31 coil)
0V.8
SB2:LED−
0V.9
W2:14(−)
0V.1
PS1:A2 (−Vo)
0V.2
K1:N/−
0V.3
SK3:A2
0V.4
SB1:LED−
0V.5
W1:14(−)
0V.6
K2:N/−
0V.7
SK4:A2
0V.8
SB2:LED−
0V.9
W2:14(−)
Spare: X1-L ×2, X1-N ×2, X2-24 ×3, X2-0V ×3. PE block is fully allocated.

## Slide 3
03 / TERMINAL ASSIGNMENTS / BOTH CHANNELS
EN1/EN2 are the switched +24 V nets OUT of Finder 13.61 terminal 14 (K1/K2). They are NOT selector-gated +24 V.
X3 = CHANNEL 1 • X4 = CHANNEL 2 / SIX SPARE POSITIONS PER CHANNEL
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 03 / 14
GATED +24 V
PTFIX 6-way red / 3273004
One input from selector, three separate loads
X3-24G / CHANNEL 1
1.
Selector S1-B:24
2.
Finder K1:L/+
3.
Finder K1:11
4.
EAO SB1:C
X4-24G / CHANNEL 2
1.
Selector S2-B:24
2.
Finder K2:L/+
3.
Finder K2:11
4.
EAO SB2:C
HEATER ENABLE (EN)
PTFIX 6-way orange / 3273018
One input from Finder output, four loads
X3-EN1 / CHANNEL 1
1.
Finder K1:14
2.
Finder 62.31 SK3:A1
3.
EAO SB1:LED+
4.
Crydom SSR1:A1/+3
5.
Activity HL1:+ (from K1:14 / EN1)
X4-EN2 / CHANNEL 2
1.
Finder K2:14
2.
Finder 62.31 SK4:A1
3.
EAO SB2:LED+
4.
Crydom SSR2:A1/+3
5.
Activity HL2:+ (from K2:14 / EN2)
SWITCHED SSR RETURN (DRV)
PTFIX 6-way violet / 3273016
Weidmüller output terminal 13 and two load returns
X3-DRV1 / CHANNEL 1
1.
Weidmüller W1:13(+)
2.
Crydom SSR1:A2/−4
3.
Activity HL1:−
X4-DRV2 / CHANNEL 2
1.
Weidmüller W2:13(+)
2.
Crydom SSR2:A2/−4
3.
Activity HL2:−
DRV1/DRV2 are controlled returns through W1/W2; neither is a direct 0 V connection.

## Slide 4
04 / MAINS SUPPLY & DISTRIBUTION
AC supply divides into three L/N destinations: the shared 24 V supply and one Omron controller per channel.
AC INPUT
DISTRIBUTION / X1
POWER SUPPLY & TWO CONTROLLER BRANCHES
L
N
PE
J1 SCHURTER
DD11.0111.1110
C14 inlet · switch · fuse
Manufacturer datasheet ↗
PE CHASSIS
Enclosure / door / DIN rail
X1 AC DISTRIBUTION
L / N / PE
X1-L: Phoenix 6-port; X1-N: Phoenix 6-port; X1-PE: WAGO earth terminal
BRANCH / CH 1
BRANCH / CH 2
L and N: 1 inlet + 3 outgoing each
PS1 MEAN WELL
XDR-120E-24 · 24 V / 5 A
Shared 24 V DC supply
Manufacturer datasheet ↗
S1-A SELECTOR
DATA ↗
Schneider XB5AD23
E1 OMRON
DATA ↗
E5CC-TQX3A5M-000
A · NO 13–14
230 V AC input
S2-A SELECTOR
DATA ↗
Schneider XB5AD23
E2 OMRON
DATA ↗
E5CC-TQX3A5M-003
A · NO 13–14
230 V AC input
L
N
PE
L IN
N IN
PE IN
PE
PE
L
N
PE
C1
C2
C3
A1 +Vo
A2 −Vo
A3 −Vo
L1
N1
13
14
11
12
L2
N2
13
14
11
12
TO SHARED PSU
CH 1 CONTROLLER
CH 2 CONTROLLER
24 V OUTPUT → SHEET 02
MAINS DISTRIBUTION / X1-L, X1-N AND X1-PE ARE THREE SEPARATE GROUPS
L/N destinations: PS1, E1 and E2. PE bonds the power supply, cabinet body and door; do not join N to PE.
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 04 / 14

## Slide 5
05 / SHARED 24 V DISTRIBUTION & CHANNEL INTERLOCKS
Shared +24 V feeds two selector inputs. Shared 0 V serves four return circuits per channel.
24 V DC DISTRIBUTION / CHANNEL 1 + CHANNEL 2
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 05 / 14
Each selector: contact A (13-14) switches the Omron mains live; contact B (23-24) gates the channel +24 V. EN1/EN2 come from Finder 13.61 terminal 14.
PS1 MEAN WELL
XDR-120E-24
24 V DC / 5 A shared supply
Manufacturer datasheet ↗
X2 DC DISTR.
+24 V / 0 V
X2-24: 6 ports, 3 used. X2-0V: 12 ports, 9 used.
S1-B SELECTOR
XB5AD23
Manufacturer datasheet ↗
CH1 CONTROL NETS
X3-24G / X2-0V
S2-B SELECTOR
XB5AD23
Manufacturer datasheet ↗
CH2 CONTROL NETS
X4-24G / X2-0V
+Vo
24+
-Vo
0 V
24+
23
23
24
24
+24
0 V
0 V
24+
23
23
24
24
+24
0 V
0 V
CH1: 24G feeds Finder L/+, 11 and SB1:C. 0 V connections terminate at X2-0V.
CH2: 24G feeds Finder L/+, 11 and SB2:C. 0 V connections terminate at X2-0V.
+24 V / gated
0 V return
B · NO 23-24
B · NO 23-24

## Slide 6
06 / CHANNEL 1 / MOMENTARY ENABLE & FINDER CONTROL
CH1: Finder 13.61 K1:14 is the EN1 switched +24 V output supplying ACTIVE LED+.
HEATER ENABLE / EN1 SHARED SWITCHED +24 V NODE
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 06 / 14
Finder 13.61: RI step mode; each valid momentary press changes heater-enable state.
CH1 CONTROL NETS
X3-24G / X2-0V
SB1 EAO + LED
82-4151.1134
Manufacturer datasheet ↗
K1 FINDER 13.61
13.61.0.024.0000
Manufacturer datasheet ↗
K3 / SK3 RELAY + SOCKET
62.31.9.024.4800
Specified relay socket: 92.03SMA
Relay PDF ↗
Socket PDF ↗
A1/A2 = 62.31 SOCKET COIL (not Crydom)
+24
C
0 V
LED−
NO
3
+24
L/+
11
14
A1
0 V
N/−
A2
LED+
EN1
EN1
K1:14 → X3-EN1 → HL1:+ (alongside relay coil A1, EAO LED+ and Crydom +3)
EN1 = K1:14 switched output; terminal group X3-EN1 distributes this to four loads including HL1:+.
X3-24G → SB1:C, K1:L/+, K1:11 | SB1:NO → K1:3 | X3-EN1 → SK3:A1, SB1:LED+, SSR1:A1/+3, HL1:+ | X2-0V → K1:N/−, SK3:A2, SB1:LED−, W1:14(−)
Gated +24 V
0 V return
Momentary input

## Slide 7
07 / CHANNEL 2 / MOMENTARY ENABLE & FINDER CONTROL
CH2: Finder 13.61 K2:14 is the EN2 switched +24 V output supplying ACTIVE LED+.
HEATER ENABLE / EN2 SHARED SWITCHED +24 V NODE
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 07 / 14
Finder 13.61: RI step mode; each valid momentary press changes heater-enable state.
CH2 CONTROL NETS
X4-24G / X2-0V
SB2 EAO + LED
82-4151.1134
Manufacturer datasheet ↗
K2 FINDER 13.61
13.61.0.024.0000
Manufacturer datasheet ↗
K4 / SK4 RELAY + SOCKET
62.31.9.024.4800
Specified relay socket: 92.03SMA
Relay PDF ↗
Socket PDF ↗
A1/A2 = 62.31 SOCKET COIL (not Crydom)
+24
C
0 V
LED−
NO
3
+24
L/+
11
14
A1
0 V
N/−
A2
LED+
EN2
EN2
K2:14 → X4-EN2 → HL2:+ (alongside relay coil A1, EAO LED+ and Crydom +3)
EN2 = K2:14 switched output; terminal group X4-EN2 distributes this to four loads including HL2:+.
X4-24G → SB2:C, K2:L/+, K2:11 | SB2:NO → K2:3 | X4-EN2 → SK4:A1, SB2:LED+, SSR2:A1/+3, HL2:+ | X2-0V → K2:N/−, SK4:A2, SB2:LED−, W2:14(−)
Gated +24 V
0 V return
Momentary input

## Slide 8
08 / CHANNEL 1 / ENABLE-GATED SSR DRIVE + ACTIVITY LED
CH1 ACTIVE LED+ supply: Finder 13.61 K1:14 → EN1 → HL1:+. LED− stays on W1-switched return.
THERMOCOUPLE / 12 V PULSE INTERFACE / EN1 ENABLED 24 V BRANCH
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 08 / 14
JTC1 TYPE K
External sensor
Type K panel connector
E1 OMRON
E5CC-TQX3A5M-000
12 V SSR demand output; TC input
Manufacturer datasheet ↗
W1 WEIDMÜLLER
8950770000
Isolated 12 V input; 13(+) to 14(−) DC switch
Manufacturer datasheet ↗
SSR1 CRYDOM
DR2220D30U
24 V input: +3/A1 and −4/A2
Manufacturer datasheet ↗
HL1 ACTIVITY LED
24 V DC, integrated resistor
RS 130-1086 • 20 mA max
K1:14 → EN1 +24 V
From Finder K1:14 via X3-EN1
X2 0 V RETURN
Shared control return
TC+
6+
TC−
5−
1+
A1
2−
A2
EN1
A1/+3
LED+
A2/−4
LED−
13+
14−
0 V
X3-DRV1: W1:13(+) / SSR1:A2(−4) / HL1:− | W1:14(−) → X2-0V
LED+ is supplied from Finder K1:14 (EN1). LED− is switched by W1.
W1 output: 100 mA maximum. SSR input plus 24 V activity lamp: up to 35 mA; use one conductor per PTFIX port.
TC / 12 V demand
EN1 from Finder K1:14
SSR1:A2 + HL1:− → X3-DRV1 → W1:13; W1:14 → X2-0V
POSITIVE SUPPLY: FINDER K1:14 (EN1)
FINDER K1:14 → X3-EN1 → HL1:+
EN1/EN2 are the switched outputs of Finder K1/K2 terminal 14.

## Slide 9
09 / CHANNEL 2 / ENABLE-GATED SSR DRIVE + ACTIVITY LED
CH2 ACTIVE LED+ supply: Finder 13.61 K2:14 → EN2 → HL2:+. LED− stays on W2-switched return.
THERMOCOUPLE / 12 V PULSE INTERFACE / EN2 ENABLED 24 V BRANCH
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 09 / 14
JTC2 TYPE K
External sensor
Type K panel connector
E2 OMRON
E5CC-TQX3A5M-003
12 V SSR demand output; TC input
Manufacturer datasheet ↗
W2 WEIDMÜLLER
8950770000
Isolated 12 V input; 13(+) to 14(−) DC switch
Manufacturer datasheet ↗
SSR2 CRYDOM
DR2220D30U
24 V input: +3/A1 and −4/A2
Manufacturer datasheet ↗
HL2 ACTIVITY LED
24 V DC, integrated resistor
RS 130-1086 • 20 mA max
K2:14 → EN2 +24 V
From Finder K2:14 via X4-EN2
X2 0 V RETURN
Shared control return
TC+
6+
TC−
5−
1+
A1
2−
A2
EN2
A1/+3
LED+
A2/−4
LED−
13+
14−
0 V
X4-DRV2: W2:13(+) / SSR2:A2(−4) / HL2:− | W2:14(−) → X2-0V
LED+ is supplied from Finder K2:14 (EN2). LED− is switched by W2.
W2 output: 100 mA maximum. SSR input plus 24 V activity lamp: up to 35 mA; use one conductor per PTFIX port.
TC / 12 V demand
EN2 from Finder K2:14
SSR2:A2 + HL2:− → X4-DRV2 → W2:13; W2:14 → X2-0V
POSITIVE SUPPLY: FINDER K2:14 (EN2)
FINDER K2:14 → X4-EN2 → HL2:+
EN1/EN2 are the switched outputs of Finder K1/K2 terminal 14.

## Slide 10
10 / CHANNEL 1 / COMPLETE DC HEATER POWER LOOP
External 0–60 V DC supply, breaker, polarity-sensitive Finder DC relay, Crydom SSR and direct return.
INDEPENDENT HEATER SUPPLY / 15 A MAX DESIGN
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 10 / 14
Finder 62.31 34(+)→14(−) and Crydom load +1→−2 are in SWITCHED DC+; neither terminal is DC−.
JP1-IN DC SUPPLY
0–60 V / up to 15 A
DC input / cable sized for 15 A
QF1 LOVATO
P1MB1PC16
16 A / 80 V DC MCB
Manufacturer datasheet ↗
K3/SK3 62.31
62.31.9.024.4800
92.03SMA socket for 62.31
Manufacturer datasheet ↗
SSR1 CRYDOM
DR2220D30U
Solid-state DC switch
Manufacturer datasheet ↗
JP1-OUT HEATER
External resistive load
DC heater output / 15 A-rated cable
DC+
1
P1-01
2
34+
P1-02
14−
+1
P1-03
−2
H+
P1-04
SSR
NO contact
Electronic switch
DC−
H−
DC NEGATIVE RETURN — SEPARATE FROM SWITCHED POSITIVE
Finder 14(−) and SSR −2 belong to the switched POSITIVE conductor, not DC negative. | Size the protective breaker, relay/socket, output connector, cable and SSR heat sink for the operating duty.
Switched positive
Separate DC− return

## Slide 11
11 / CHANNEL 2 / COMPLETE DC HEATER POWER LOOP
External 0–60 V DC supply, breaker, polarity-sensitive Finder DC relay, Crydom SSR and direct return.
INDEPENDENT HEATER SUPPLY / 15 A MAX DESIGN
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 11 / 14
Finder 62.31 34(+)→14(−) and Crydom load +1→−2 are in SWITCHED DC+; neither terminal is DC−.
JP2-IN DC SUPPLY
0–60 V / up to 15 A
DC input / cable sized for 15 A
QF2 LOVATO
P1MB1PC16
16 A / 80 V DC MCB
Manufacturer datasheet ↗
K4/SK4 62.31
62.31.9.024.4800
92.03SMA socket for 62.31
Manufacturer datasheet ↗
SSR2 CRYDOM
DR2220D30U
Solid-state DC switch
Manufacturer datasheet ↗
JP2-OUT HEATER
External resistive load
DC heater output / 15 A-rated cable
DC+
1
P2-01
2
34+
P2-02
14−
+1
P2-03
−2
H+
P2-04
SSR
NO contact
Electronic switch
DC−
H−
DC NEGATIVE RETURN — SEPARATE FROM SWITCHED POSITIVE
Finder 14(−) and SSR −2 belong to the switched POSITIVE conductor, not DC negative. | Size the protective breaker, relay/socket, output connector, cable and SSR heat sink for the operating duty.
Switched positive
Separate DC− return

## Slide 12
12 / CONNECTION SCHEDULE / MAINS + 24 V DISTRIBUTION
Terminal references for the three mains destinations, the 24 V supply and two independent control channels.
TERMINAL-LEVEL REFERENCE / MAINS AND 24 V
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 12 / 14
Terminal positions on X1/X2 and X3/X4 are assigned individually on Sheets 02 and 03.
AC01
J1 switched fused L
→
X1-L: mains live (brown block)
AC02
J1 switched N
→
X1-N: mains neutral (blue block)
AC03
J1:PE
→
X1-PE: cabinet protective earth
AC04
X1:L / N / PE
→
PS1:C1 (L), C2 (N), C3 (PE)
AC05
X1:L → S1-A:13→14
→
E1:11 (L)
AC06
X1:N bus
→
E1:12 (N)
AC07
X1:L → S2-A:13→14
→
E2:11 (L)
AC08
X1:N bus
→
E2:12 (N)
DC01
PS1:A1 +Vo
→
X2-24 common +24 V
DC02
PS1:A2/A3 −Vo
→
X2-0V common return
DC03
X2:+24 → S1-B:23/24*
→
X3-24G gated +24 V
DC04
X2:+24 → S2-B:23/24*
→
X4-24G gated +24 V
DC05
X2:0 V shared
→
K1/K2, SK3/SK4, SB1/SB2 and W1/W2
Mains: one inlet and three outgoing circuits for L and N. Common +24 V: one in and two out. Common 0 V: one in and eight out.

## Slide 13
13 / CONNECTION SCHEDULE / CONTROLS + HEATER
Functional point-to-point schedule for both control channels and the 0–60 V DC heater power circuits.
TERMINAL-LEVEL REFERENCE / CHANNELS 1 AND 2
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 13 / 14
All multiway nets are assigned to their own distribution groups; one conductor uses one terminal position.
ENABLE / EACH CH
X3-24G / X4-24G → Finder L/+, 11 and button C. X2-0V → Finder N/−, 62.31 coil A2, EAO LED− and Weidmüller 14(−).
MOMENTARY INPUT
EAO NO → Finder 13.61 terminal 3; EAO C is fed by its channel gated +24 V distribution group.
FINDER OUTPUT
CH1: Finder 13.61 K1:14 → X3-EN1 → HL1:+; CH2: Finder K2:14 → X4-EN2 → HL2:+. EN also supplies 62.31 coil, EAO LED and SSR input.
THERMOCOUPLE
Type K sensor (+) → E1/E2:6; sensor (−) → E1/E2:5.
OMRON / WEIDMÜLLER
Omron E1/E2 SSR demand 1(+), 2(−) → Weidmüller W1/W2 A1(+), A2(−): isolated 12 V control.
WEID / SSR DRIVE
EN1 = K1:14; EN2 = K2:14. HL1/HL2 positives are EN loads (NOT selector 24G); negatives via X3/X4-DRV → W1/W2:13 → W:14 → X2-0V.
DC POSITIVE
Supply DC+ → Lovato 1→2 → Finder 62.31 contact 34 (+)→14 (−) → SSR +1→−2 → heater+.
DC RETURN
Heater− → matching external DC supply−; Finder 14 and SSR −2 are NOT DC−.
DC COIL
62.31 socket A1/A2 is the 24 V DC relay coil; Crydom A1/A2 is SSR control, NOT the power contact.
Mains, control +24, 0 V, driver returns, and external DC heater power are separate circuits.

## Slide 14
14 / COMPONENT REFERENCES & MAINTENANCE
PTFIX-based distribution and independent two-channel control: functional and terminal reference.
COMPONENT REGISTER / WIRING & SERVICE INFORMATION
REFERENCE WIRING / 230 V AC CONTROL SUPPLY • 24 V DC CONTROLS • 0–60 V DC HEATER CIRCUITS
HEATING RATE CONTROLLER / REFERENCE ELECTRICAL WIRING / R1.2 · 26 OCT 2026
SHEET 14 / 14
Schurter DD11.0111.1110
Datasheet ↗
Mean Well XDR-120E-24
Datasheet ↗
Schneider XB5AD23 ×2
Datasheet ↗
Omron E5CC-TQX3A5M-000 / -003
Datasheet ↗
EAO 82-4151.1134 ×2
Datasheet ↗
Finder 13.61.0.024.0000 ×2
Datasheet ↗
Finder 62.31.9.024.4800 ×2
Datasheet ↗
Weidmüller 8950770000 ×2
Datasheet ↗
Crydom DR2220D30U ×2
Datasheet ↗
Lovato P1MB1PC16 ×2
Datasheet ↗
INSTALLATION & MAINTENANCE ESSENTIALS
01
Protective earth: J1 inlet, PS1, enclosure body and door bond all connect to X1-PE.
02
Mains distribution: PSU, Omron E1 and Omron E2 each have their own live and neutral branch.
03
Control: common +24 V and 0 V; plus separate gated +24, EN and SSR driver-return nodes per channel.
04
ACTIVE LED+: Finder K1/K2:14 → EN1/EN2 → HL1/HL2+. LED− is switched via W1/W2.
05
Before servicing: isolate mains AND both external DC supplies; check PE, connectors, wiring and SSR cooling.
HL1/HL2 specified: RS PRO 130-1086 yellow LED, 24 V DC, max 20 mA, IP67; 14 mm mounting hole.
Finder 92.03SMA relay socket datasheet ↗